## Sheet1
寄存器地址 | 描述 | 小数点 | 数据类型
13312 | V1/V12 Voltage | U1 | UINT32 | U1 | 1位小数
13314 | V2/V23 Voltage | U1 | UINT32 | U2 | 2位小数
13316 | V3/V31 Voltage | U1 | UINT32 | U3 | 3位小数
13318 | I1 Current | U2 | UINT32
13320 | I2 Current | U2 | UINT32
13322 | I3 Current | U2 | UINT32
13324 | kW L1 | U3 | INT32
13326 | kW L2 | U3 | INT32
13328 | kW L3 | U3 | INT32
13330 | kvar L1 | U3 | INT32
13332 | kvar L2 | U3 | INT32
13334 | kvar L3 | U3 | INT32
13336 | kVA L1 | U3 | UINT32
13338 | kVA L2 | U3 | UINT32
13340 | kVA L3 | U3 | UINT32
13342 | Power factor L1 | ×0.001 | INT32
13344 | Power factor L2 | ×0.001 | INT32
13346 | Power factor L3 | ×0.001 | INT32
13348 | V1/V12 Voltage THD | ×0.1% | UINT32
13350 | V2/V23 Voltage THD | ×0.1% | UINT32
13352 | V3/V31 Voltage THD | ×0.1% | UINT32
13354 | I1 Current THD | ×0.1% | UINT32
13356 | I2 Current THD | ×0.1% | UINT32
13358 | I3 Current THD | ×0.1% | UINT32
13360 | I1 K-Factor | ×0.1 | UINT32
13362 | I2 K-Factor | ×0.1 | UINT32
13364 | I3 K-Factor | ×0.1 | UINT32
13366 | I1 Current TDD | ×0.1% | UINT32
13368 | I2 Current TDD | ×0.1% | UINT32
13370 | I3 Current TDD | ×0.1% | UINT32
13372 | V12 Voltage | U1 | UINT32
13374 | V23 Voltage | U1 | UINT32
13376 | V31 Voltage | U1 | UINT32
13696 | Total kW | U3 | INT32
13698 | Total kvar | U3 | INT32
13700 | Total kVA | U3 | UINT32
13702 | Total PF | ×0.001 | INT32
13704 | Total PF lag | ×0.001 | UINT16
13706 | Total PF lead | ×0.001 | UINT16
13708 | Total kW import | U3 | UINT32
13710 | Total kW export | U3 | UINT32
13712 | Total kvar import | U3 | UINT32
13714 | Total kvar export | U3 | UINT32
13716 | 3-phase average L-N/L-L voltage | U1 | UINT32
13718 | 3-phase average L-L voltage | U1 | UINT32
13720 | 3-phase average current | U2 | UINT32
13824 | Not used
13826 | In (neutral) Current | U2 | UINT32
13828 | Frequency | ×0.01Hz | UINT32
13830 | Voltage unbalance | % | UINT32
13832 | Current unbalance | % | UINT32
13864 | V1/V12 Voltage magnitude | U1 | UINT32
13866 | V2/V23 Voltage magnitude | U1 | UINT32
13868 | V3/V31 Voltage magnitude | U1 | UINT32
13870 | Not used
13872 | I1 Current magnitude | U2 | UINT32
13874 | I2 Current magnitude | U2 | UINT32
13876 | I3 Current magnitude | U2 | UINT32
13878 | Not used
13880 | V1/V12 Voltage angle | ×0.1º | INT32
13882 | V2/V23 Voltage angle | ×0.1º | INT32
13884 | V3/V31 Voltage angle | ×0.1º | INT32
13886 | Not used | R
13888 | I1 Current angle | ×0.1º | INT32
13890 | I2 Current angle | ×0.1º | INT32
13892 | I3 Current angle | ×0.1º | INT32
13894 | Not used